APT REPORT ON

GREEN DATA CENTRE PRACTICES

AND CLIMATE RESILIENCE IN THE ASIA-PACIFIC REGION

Edition: April 2026

The 38th APT Standardization Program Forum (ASTAP-38)

20 – 24 April 2026

Bangkok, Thailand

(Source: ASTAP-381/OUT-09)

No. APT/ASTAP/REPT-43 (Rev.1)

Table of Contents

1	Scope	2

2	Terms and Definitions	2

2.1	A Data Center	2

2.2	A Green data centre	2

2.3	Power density	2

2.4	Space efficiency	2

2.5	Power Usage Effectiveness (PUE)	2

2.6	Carbon Usage Effectiveness (CUE)	2

2.7	Water Usage Effectiveness (WUE)	2

2.8	Tropical Climate Adaptation	2

2.9	Building-Integrated Photovoltaics (BIPV)	3

2.10	Liquid Cooling Maturity Model (LCMM)	3

2.11	Data Center Resource Effectiveness (DCRE)	3

2.12	Digital Twin	3

2.13	Computational Fluid Dynamics (CFD) Simulation	3

2.14	Combined Cooling, Heat, and Power (CCHP)	3

3	Overview of Related International Standardization Activities on Green Data Centre	4

3.1	ITU-T	4

3.2	ISO/IEC JTC1	4

3.3	ETSI	5

3.4	ANSI/TIA	6

3.5	LEED	6

3.6	The Green Grid	6

3.7	Uptime Institute	7

4	National Policies, Laws, Regulations and Management Systems of Member Countries  and Example Initiative	8

4.1	Malaysia	8

4.1.1	Historical Baseline: Study of the Carbon Footprint (2015)	8

4.1.2	Technical Code for the Specification for Green Data Centres	10

4.1.3	Malaysia	10

4.2	Bhutan	11

4.3	Sri Lanka	11

4.4	Myanmar	11

4.5	Vietnam	11

4.6	Brunei	12

4.7	Indonesia	12

4.8	Japan	13

5	Analysis of Further Study	13

6	References	14

# Scope

The scope of this report covers efforts in Asia Pacific region such as policies and activities on the Green Data Centre (GDC) in the ICT/Telecommunication sector. In alignment with WTSA-24 Resolution 73, this edition provides updated information on sustainable practices and environmental resilience tailored for the region's diverse climates.

This update incorporates regional insights on climate adaptation from Malaysia, Bhutan, Sri Lanka, Myanmar, Vietnam, Brunei, and Indonesia. It covers shared climate and disaster risks, technology and mitigation strategies—including Digital Twins, CFD Simulation, and CCHP—and renewable energy solutions, such as Solar PV and BIPV, that are practical for each country's unique environment. The report further identifies operational challenges and technical specifications currently deployed across the region to support ASTAP’s goal of harmonizing ICT standards and promoting practical solutions for APT member countries.

# Terms and Definitions

## A Data Center

A repository for the storage, management and disseminations of data.

## A Green data centre

A repository for the storage, management, and dissemination of data in which the mechanical, lighting, electrical and computer systems are designed for maximum energy efficiency and minimum environmental impact.

## Power density

The energy consumption of ICT equipment per rack cabinet of floor area of a server room.

## Space efficiency

The ratio of floor area employed for ICT equipment in relation to the total floor area of the building.

## Power Usage Effectiveness (PUE)

The ratio of total amount of energy used by a computer data center facility to the energy delivered to computing equipment.

## Carbon Usage Effectiveness (CUE)

A measure of data center sustainability in terms of data center specific carbon emissions. CUE is calculated by dividing the “total CO2 emissions caused by total data center energy” by the “energy consumption of the IT computing equipment”.

## Water Usage Effectiveness (WUE)

A metric used to determine the amount of water used by the facility for cooling and other operational needs relative to the IT equipment energy consumption

## Tropical Climate Adaptation

Architectural designs and technical solutions specifically engineered to mitigate the operational impacts of high ambient temperatures, extreme humidity (>80%), and heavy rainfall prevalent in equatorial regions.

## Building-Integrated Photovoltaics (BIPV)

Photovoltaic materials used to replace conventional building materials in parts of the building envelope, such as the roof, skylights, or facades, serving as both a structural component and a renewable energy source.

## Liquid Cooling Maturity Model (LCMM)

A strategic framework designed to guide the adoption of advanced thermal management technologies, providing a staged approach for transitioning from air cooling to various levels of liquid-cooling integration.

## Data Center Resource Effectiveness (DCRE)

A unified assessment framework and scoring tool that combines multiple performance indicators—including energy, water, and carbon—to provide a holistic view of a facility's resource efficiency and sustainability maturity.

## Digital Twin

A virtual 3D replica of a physical data centre that mirrors real-time operational conditions—including power, cooling, and IT load—to simulate behavior, optimize performance, and predict future states without impacting current operations.

## Computational Fluid Dynamics (CFD) Simulation

A simulation-based modeling technology that solves complex numerical equations to predict airflow, temperature distribution, and heat transfer within a space. In data centres, it is used to identify potential hot spots and optimize cooling performance during both the design and operational phases.

## Combined Cooling, Heat, and Power (CCHP)

An integrated energy system that uses a single fuel source, such as gas, to simultaneously produce electricity and useful thermal energy for cooling. In data centers, waste heat is recovered via heat exchangers to drive absorption chillers, significantly reducing the reliance on grid power for thermal management, as illustrated by the energy distribution flow in Figure 1.

Figure 1 Sankey Diagram of Energy Distribution and Thermal Recovery Potential in CCHP Systems

# Overview of Related International Standardization Activities on Green Data Centre

## ITU-T

Recommendation ITU-T L.1300 describes best practices aimed at reducing the negative impact of data centers on the climate. The application of the best practices defined in this document can help owners and managers to build future data centers, or improve existing ones, to operate in an environmentally responsible manner.

This Recommendation describes best practices for energy-efficient construction, operation and management of green data centres that contain a number of essential components, including ICT equipment and services, cooling, power equipment, data centre building, etc.

Best practices have been identified and divided into different clauses to cover the following different components of a data centre:

- planning, utilization and management;

- ICT equipment and services;

- cooling;

- data centre power equipment;

- other data centre equipment;

- data centre building;

- monitoring;

- design of network;

- cloud data centre;

- optimization of energy management of the whole data centre.

In alignment with WTSA-24 Resolution 73, ITU-T has expanded its framework to address the circular economy and climate-resilient infrastructure. Key additions to the ITU-T L-series include:

- ITU-T L.1333 (2022): Introduces the Network Carbon Intensity energy (NCIe) metric, allowing operators to monitor carbon data intensity alongside energy efficiency to align with global net-zero trajectories.

- ITU-T L.1327 (2024): Provides a specific methodology for the selection of cooling technologies. It includes a dedicated focus on Tropical Climate Adaptation, identifying that traditional free cooling is often impractical in equatorial regions and recommending advanced alternatives such as liquid cooling and immersion systems.

- ITU-T L.1395 & L.1396 (2025): Establish standardized monitoring and control interfaces for power, cooling, and building environment systems. These recommendations focus on the interoperability of heterogeneous management systems in multi-vendor environments, enabling more precise automated adjustments to optimize energy consumption in challenging climates.

## ISO/IEC JTC1

ISO/IEC JTC 1 is a joint technical committee of the International Organization for Standardization (ISO) and the International Electrotechnical Commission (IEC). Its purpose is to develop, maintain and promote standards in the fields of information technology (IT) and Information and Communications Technology (ICT).

ISO/IEC JTC1 has significantly expanded its data centres energy efficiency KPI series (ISO/IEC 30134) and its infrastructure standards (ISO/IEC 22237). The current series includes:

- ISO/IEC 30134-1:2016+A1:2018 Part 1: Overview and general requirements.

- ISO/IEC 30134-2:2026 Part 2: Power Usage Effectiveness (PUE).

- ISO/IEC 30134-3:2016+A1:2018 Part 3: Renewable Energy Factor (REF).

- ISO/IEC 30134-4:2017+A1:2025 Part 4: IT Equipment Energy Efficiency for servers (ITEEsv).

- ISO/IEC 30134-5:2017+A1:2025 Part 5: IT Equipment Utilization for servers (ITEUsv).

- ISO/IEC 30134-6:2021 Part 6: Energy Reuse Factor (ERF).

- ISO/IEC 30134-7:2023 Part 7: Cooling Efficiency Ratio (CER).

- ISO/IEC 30134-8:2022 Part 8: Carbon Usage Effectiveness (CUE).

- ISO/IEC 30134-9:2022 Part 9: Water Usage Effectiveness (WUE).

- ISO/IEC 22237-1:2021 Information Technology – Data centre facilities and infrastructures – Part 1: General concepts.

- ISO/IEC TS 22237-31:2026 Information Technology – Data centre facilities and infrastructures – Part 31: Key performance indicators for resilience.

## ETSI

ETSI, the European Telecommunications Standards Institute, produces globally-applicable standards for Information and Communications Technologies (ICT), including fixed, mobile, radio, converged, broadcast and internet technologies.

ETSI is a not-for-profit organization with more than 900 ETSI member organizations drawn from 62 countries across 5 continents world-wide.

ETSI, a major actor in Information and Communication Technology standardization (ICT), has recently published the DCEM (Data Centre Energy Management) indicator standard, to measure energy efficiency and compare energy management efficiency in data centres.

This indicator, the DCEM Global KPI, has been developed by ETSI’s OEU (Operational Energy efficiency for Users) Industry Specification Group and is defined in ETSI GS OEU 001. This group comprises ICT companies from various sectors including banking, telecommunications, the automotive and the aeronautical industry.

The DCEM Global KPI specifies the coefficient or ‘Global KPI’ of the eco-efficiency and energy management of data centres. It combines two indicators: one taking into account different sizes of data centre (S, M, L or XL) and a second incorporating 9 different levels of performance, similar to the energy classification model used for home appliances. The DCEM Global KPI meets a twofold objective: to assess the level of eco-efficiency in data centres, and to allow benchmarking of data centres or ITC locations in a wide range of industrial sectors.

The DCEM Global KPI is based on a formula with 4 different component KPIs defined in the new ETSI Standard ES 205 200-2-1:

- Energy consumption, KPIEC

- Task efficiency, KPITE

- Energy reused, KPIREUSE

- Renewable energy, KPIRE

To address emerging requirements for environmental resilience and transparency, ETSI has introduced additional standards:

- ETSI GS OEU 020: Specifies the Carbon equivalent Intensity measurement (KPICE) for operational infrastructures. This provides a Global KPI for ICT sites to monitor and report their carbon footprint alongside energy efficiency metrics.

- ETSI EN 305 174-2: This standard is part of the Broadband Deployment and Lifecycle Resource Management series. It specifically addresses ICT sites, providing a framework for managing the environmental impact of data centres throughout their entire operational lifecycle, including the sustainable management of end-of-life equipment.

## ANSI/TIA

The American National Standards Institute is a private non-profit organization that oversees the development of voluntary consensus standards for products, services, processes, systems, and personnel in the United States. In 2005, The Telecommunication Industry Association announced ANSI/TIA-942, the telecommunication infrastructure standards for data centre.

The ANSI/TIA-942 standard is recognized by the American National Standards Institute (ANSI) and specifies detailed guidelines for planning and building telecommunications infrastructure such as multi-tenant data centres. The standard is regularly updated through the work of a designated sub-committee and is designed through a consensus-based approach. The latest version is ANSI/TIA-942-C, which was published in May 2024.

The ANSI/TIA-942-C specification references private and public domain data center requirements for applications and procedures such as:

  - Network architecture and telecommunications infrastructure

  - Electrical design

  - Mechanical systems and environmental control

  - Building architecture and site selection

  - System redundancy and resiliency levels

  - Physical security and monitoring.

  - Fire protection and safety.

  - Sustainability and climate resilience

## LEED

- LEED or Leadership in Energy and Environmental Design, is the most widely used green building rating system in the world. Available for virtually all building, community and home project types, LEED provides a framework to create healthy, highly efficient and cost-saving green buildings. LEED certification is a globally recognized symbol of sustainability achievement. LEED is a globally recognized symbol of excellence in green buildings. LEED certification ensures electricity cost savings, lower carbon emissions and a healthier environment. The updated LEED v5 framework further enhances these objectives by prioritizing climate resilience and decarbonization through mandatory environmental risk assessments and the monitoring of both operational and embodied carbon.

## The Green Grid

The Green Grid is an affiliate membership level of the Information Technology Industry Council (ITI), a premier trade association that works to advance public policies for the tech sector. ITI’s Green Grid works to improve IT and data center energy efficiency and eco-design around the world. It is an open industry consortium of information and communications technology (ICT) industry end-users, policymakers, technology providers, facility architects, and utility companies.

The Green Grid, the data center industry group known best for creating the industry’s most popular data center efficiency metric, Power Usage Effectiveness (PUE), has developed a new metric for data center operators, called Performance Indicator (PI).

The Green Grid published PUE in 2007. Since then, the metric has become widely used in the data center industry. Unlike PUE, which focuses on both cooling and electrical infrastructure, PI is focused on cooling. The Green Grid’s aim in creating it was to address the fact that efficiency isn’t the only thing data center operators are concerned with. Efficiency is important to them, but so are performance of their cooling systems and their resiliency.

Expanding its focus on sustainability, The Green Grid in 2010 announced the creation of two new metrics to measure carbon and water use in data centers. The new metrics, Carbon Usage Effectiveness (CUE) and the Water Usage Effectiveness (WUE), are designed to build upon the momentum of The Green Grid’s widely-used Power Usage Effectiveness (PUE) metric.

With the new metrics, The Green Grid is broadening its efforts to take a more holistic view of data center sustainability. CUE will help data center managers determine the amount of greenhouse gas emissions generated in delivering work from the IT gear in a data center facility. Similarly, WUE will help managers determine the amount of water used by the facility, and the amount used to deliver work from IT operations.

To address evolving infrastructure needs, The Green Grid has recently introduced the Liquid Cooling Maturity Model (LCMM) to guide the adoption of advanced thermal management in high-density environments and the Data Center Resource Effectiveness (DCRE) framework, which provides a unified assessment of energy, water, and carbon impact.

## Uptime Institute

Uptime Institute is an American professional services organization best known for its "Tier Standard” and the associated certification of data center compliance with the standard.

The data center Tier standards are a standardized methodology used to determine availability in a facility. It offers companies a way to measure return on investment (ROI) and define desired levels of delivered performance. As of early 2026, more than 4,000 data centers worldwide have formally certified their data centers using the Tier standard.

There are three parts of the Tier certification process:

- Tier Certification of Design Documents - typically the first step in the Tier process and used to align the design and construction of a new facility with an organization's business needs.

- Tier Certification of Constructed Facility - the final part of the process which assures that the actual constructed data centers delivers the results specified in the Tier Standard: Topology specification.

- Tier Certification of Operational Sustainability – an assessment of the behaviors and risks intrinsic to data center operations, focusing on management, maintenance, and site-specific environmental factors to ensure long-term performance.

The Tier certifications are awarded in four levels:

- Tier IV - Fault tolerant site infrastructure

- Tier III - Concurrently maintainable site infrastructure

- Tier II - Redundant capacity components site infrastructure (redundant)

- Tier I - Basic site infrastructure (non-redundant)

# National Policies, Laws, Regulations and Management Systems of Member Countries  and Example Initiative

## Malaysia

### Historical Baseline: Study of the Carbon Footprint (2015)

The findings from the 2015 study remain in this report to serve as the historical baseline for energy efficiency efforts in Malaysia. This foundational study was conducted by the Malaysia Technical Standards Forum Bhd (MTSFB) and its Green ICT Working Group, in collaboration with the Sustainable Energy Development Authority (SEDA Malaysia) and the Malaysian Communications and Multimedia Commission (MCMC), to analyze the carbon footprint of sample Data Centres in Malaysian Government Offices.

The primary objective was to evaluate the energy used to operate data centres (DC) by placing measuring equipment on electrical distribution boards (DB) to record consumption for ICT equipment, lighting, cooling, and power. Concurrently, the study logged ambient temperature and humidity levels within the data centre environment to determine the impact of environmental factors on operational efficiency. These baseline findings and the resulting best practice recommendations are detailed below as a reference point for the region's technical evolution:

- Baseline findings

The findings of the study are as shown in charts and tables below.

Figure 2 Energy consumption based on percentage

Figure 3 Estimated Annual Consumption (kWh)

Table 1.1 is prepared by the Uptime Institute as part of the certification process of the data centres in industry.

Table 1.1 Uptime Institute Levels of Efficiency Ratings charts

| Current PUE & DcIE |  |  |
| --- | --- | --- |
| PUE | DcIE | Level of Efficiency |
| 3.0 | 33.3% | Very In-efficient |
| 2.5 | 40% | In-efficient |
| 2.0 | 50% | Average |
| 1.5 | 67.6% | Efficient |
| 1.2 | 83% | Very Efficient |

The Power Usage Effectiveness (PUE) is a ratio of the total energy used by the Data Centre (DC) to the energy used by the IT equipment.

PUE = Total Energy Consumption by Data Centre (kWh)Total Energy Consumption by IT Devices (kWh)

The PUE for the data centres is as below.

Figure 4 Power Usage Effectiveness

- Best Practice Recommendations

Recommendations on potential energy saving measures are list in the table below.

Table 1.2 Potential Energy Saving Measures

| Site Name | Improve air flow and Increase AC Setpoint | Server Power Mgmt S/W | Inverter for ACSU | Portable Dehumidifier | Increase AC Setpoint in UPS Room | Insulate Window Area | Partition DC and Realign Cabinets | Partition under floor air plenum | Replace Glass/ Plastic Doors with Grill | Relocate In Row AC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X | X | X |  | X |  |  |  |
| 2 | X | X | X | X | X |  | X |  |  |  |
| 3 | X | X |  | X |  |  |  |  |  | X |  |
| 4 | X | X |  | X |  |  |  |  |  |  |
| 5 | X | X |  | X | X |  |  |  |  |  |
| 6 | X | X |  | X | X | X | X | X | X |  |
| 7 | X | X |  | X |  |  | X |  | X |  |
| 8 | X | X |  | X |  | X | X | X | X |  |
| 9 |  |  |  |  |  |  |  |  |  | X |
| 10 | X | X | X | X | X |  | X | X | X |  |

### Technical Code for the Specification for Green Data Centres

Building upon the initial 2015 study, Malaysia has formalized its green data centre requirements through the MCMC MTSFB TC G004:2024 – Specification for Green Data Centres (First Revision). This technical code, developed by the Malaysian Technical Standards Forum Bhd (MTSFB), provides the current minimum requirements for green data centres to establish systems and processes that improve energy efficiency while reducing the industry's environmental impact.

To further the efforts of greening the ICT and telecommunications sector, the following key updates are prioritized:

- Refined Efficiency Benchmarks: The specification recommends a design Power Usage Effectiveness (PUE) of ≤1.5 for new tropical data centres—a significant advancement from the 2.0 baseline recorded in 2015. It also incorporates Water Usage Effectiveness (WUE) to ensure that the high water demand of cooling systems in equatorial climates is properly monitored and managed.

- High-Density Tropical Cooling: The code provides guidance on transitioning to advanced thermal management solutions, such as Liquid Cooling (Immersion or Direct-to-Chip) and Precision Air Conditioning (PAC). These technologies are highlighted as critical for supporting 5G and AI infrastructure while overcoming the efficiency limitations of traditional air cooling in high-humidity environments.

- Decarbonization and Resource Strategy: The revision encourages the integration of Renewable Energy (RE), including on-site Solar PV and Building-Integrated Photovoltaics (BIPV). It also emphasizes the use of Carbon Usage Effectiveness (CUE) to track and minimize the carbon footprint of the data centre power chain, supporting long-term national sustainability goals.

### Malaysia

Malaysia manages a diverse infrastructure portfolio, including Hyperscale, Colocation, and Enterprise facilities, with a focus on regional sustainability benchmarks:

- Climate & Disaster Resilience: The primary focus is Tropical Climate Adaptation, with facilities engineered to withstand high humidity and extreme temperatures. These atmospheric conditions are identified as the main challenges preventing the use of traditional free-cooling

- Technological Mitigation: Current efforts prioritize the deployment of Liquid Cooling and Air/Water-cooled precision A/C. The sector is also shifting toward Modular architectures (IMDC/OMDC) and the adoption of Lithium-ion batteries and AI/Automation to optimize energy use.

- Structural Adaptations: To maintain operational continuity, new developments are incorporating elevated and flood-resistant designs to mitigate monsoon-related risks.

- Renewable Energy Integration: Greening of the power chain is driven by the integration of Solar PV and Hydro Electricity, with major operators actively pursuing Power Purchase Agreements (PPAs).

- Operational Challenges: The sector continues to navigate water supply scarcity and the high power consumption required for humidity control in a heat-intensive environment where "zero free-cooling" is the baseline.

## Bhutan

Bhutan’s response highlights a unique mountain-climate strategy for green ICT infrastructure:

- Mountain-Climate Cooling: Leveraging its high-altitude geography, Bhutan utilizes natural air cooling and virtualization to minimize its carbon footprint.

- Renewable Power: The entire data centre sector is 100% powered by hydro and solar energy, reporting no major adoption challenges regarding green energy.

- Disaster Risks: Primary risks identified include high rainfall, flooding, landslides, and earthquakes.

## Sri Lanka

Sri Lanka’s submission focuses on energy management and atmospheric resilience:

- Thunderstorm Protection: A unique focus is placed on lightning and thunderstorm protection given the local climate.

- Operational Efficiency: The sector uses AI energy management, modular designs, and flood-resistant structures in urban areas to maintain efficiency.

## Myanmar

Myanmar emphasizes modularity and seismic resilience for critical ICT sites:

- Relocatable Infrastructure: Deployment of relocatable container-based data centres designed to withstand 8.0 magnitude earthquakes.

- Solar Pilot Projects: Current efforts include the integration of Solar PV and the piloting of solar-assisted UPS systems.

## Vietnam

Vietnam utilizes high-level simulation to manage extreme tropical weather:

- Predictive Simulation: Use of Digital Twin & CFD simulations for climate impact prediction.

- Flood Mitigation: New facilities are constructed on platforms elevated by more than 1.5 metres to counter seasonal flooding risks.

## Brunei

Brunei’s efforts are concentrated within its unified national network:

- Structural Resilience: Focus on modular architecture and elevated flood-resilient facility designs to ensure operational stability against flood risks.

- Energy Balance: While Solar PV and hydro are integrated, current renewable costs remain a challenge compared to grid parity.

## Indonesia

Indonesia’s submission emphasizes advanced technological integration to manage high-density loads and extreme seismic risks:

- Seismic and Structural Resilience: Data center structures are engineered to withstand 8.5 magnitude earthquakes. New developments also incorporate weather and natural risk factors, such as elevated designs, to mitigate tropical flood risks.

- Innovative Energy Systems (CCHP): Deployment of Combined Heat and Power (CCHP) systems using gas engines to simultaneously produce electricity and cooling via waste heat recovery, as illustrated in the energy distribution flow in Figure 1. This pilot targets a design PUE of 1.25 for a 12 MW IT loads within a 14.5 MW total capacity facility, utilizing the technical configuration shown in Figure 5.

- Operational Efficiency: Implementation of low-load strategies, maintaining temperatures at the upper band range, and utilizing environmentally friendly refrigerants. Real-time management is supported through the integration of IoT devices with AI.

- Energy Diversification: Integration of a diverse renewable mix including Solar PV, Hydroelectricity, Biomass, and Geothermal energy. Primary challenges include the distance of facilities from energy sources and the need for regulatory fiscal incentives.

- National Standards (SNI): The sector continues to build upon the 2019 Indonesian National Standard (SNI) for Data Centers and Green Building Council Indonesia frameworks. This includes maintaining a baseline PUE < 1.5 and utilizing dynamic rotary UPS systems to provide greener power without lead-based batteries.

Figure 5 Technical Schematic for a 14.5MW Total Capacity Data Center (12 MW IT Load) utilizing CCHP to achieve a 1.25 PUE Target

## Japan

Japan performed comparative analysis between a data centre with some energy saving technology and a data centre with conventional technology by hybrid LCA method and these results were consented to be published as a Supplement to L.1410, named “Case study: a hybrid approach based comparative analysis of the environmental impact of a baseline datacenter and an energy-efficient data center”.

The Recommendation ITU-T L.1410 deals with environmental life cycle assessments (LCAs) of information and communication technology (ICT) goods, networks and services.

# Analysis of Further Study

The energy consumption of the ICT sector, particularly data centres, continues to increase globally due to more internet and broadband communication. The rapidly expanding data centre industry in the Asia Pacific remains a primary driver for global energy demand, with the region now consuming approximately 30% of the world's data centre energy as it scales to meet AI and cloud requirements. Consequently, operational costs have been heavily impacted by the rising costs of energy, making policy action essential to limit consumption growth.

Against this trend, it is important to adopt policy actions to improve the energy efficiency of data centres and limit the energy consumption growth. Data centres and IT equipment are becoming increasingly energy-efficient, and there are a variety of metrics, standards, and certifications that have emerged such as PUE, CUE, WUE, LEED, and Energy Star. Standards and metrics are important to enable the accurate measurement and comparison of data centres and IT equipment and, along with certification programs, can maintain the integrity of tech companies’ claims for energy efficiency.

Moving forward, further study is required to enhance the regional scalability of Liquid Cooling and the standardization of climate-resilient infrastructure for flood and seismic protection. ASTAP member countries’ approach offers a practical, tropical-focused strategy for green data centres, supporting ASTAP’s standardization goals. By recommending climate-specific solutions, such as Digital Twins and AI automation, and sharing regional best practices, this report enhances Asia-Pacific ICT sustainability and cooperation.

# References

- APT/ASTAP-38: Questionnaire Summary on Green Data Center Practices and Climate Resilience in the Asia-Pacific Region, Feb 2026.

- Recommendation ITU-T L.1300: Best Practices on Green Data Centre, Web Feb 2026, https://www.itu.int/rec/T-REC-L.1300

- ITU-T WTSA-24 Resolution 73: Information and communication technologies, environment, climate change and circular economy, 2024.

- ISO/IEC TS 22237:2024, Information technology — Data centre facilities and infrastructures, Web Feb 2026, https://www.iso.org/standard/81935.html

- ISO/IEC 30134:2024, Information technology — Data centres — Key performance indicators (Series Update), Web Feb 2026, https://www.iso.org/standard/82541.html

- ETSI ES 205 200-1: Access, Terminals, Transmission and Multiplexing (ATTM); Energy management; Global KPIs.

- MCMC MTSFB TC G004:2024 – Specification for Green Data Centres (First Revision), Malaysian Communications and Multimedia Commission, 2024.

- U.S. Green Building Council (USGBC), LEED v5 Green Building Rating System: Resilience and Decarbonization Framework, 2025.

- The Green Grid: Liquid Cooling Maturity Model (LCMM) and Data Center Resource Effectiveness (DCRE) Framework, Web Jan 2026.

- Performance Indicator (PI), The Green Grid Metric for Cooling Resilience, Web Jan 2026, https://www.thegreengrid.org/metrics

- Uptime Institute Tier Certifications, Web Feb 2026, https://uptimeinstitute.com/tiers

- ETSI releases the first global KPI on energy-efficiency in ICT, Web 26 May 2019 https://www.etsi.org/newsroom/news/798-2014-06-press-etsi-releases-the-first-global-kpi-on-energy-efficiency-in-ict

- Performance Indicator, Green Grid’s New Data Center Metric, Explained, Web 26 May 2019, https://www.datacenterknowledge.com/archives/2016/07/18/performance-indicator-green-grids-new-data-center-metric-explained

- Green Grid Creates Metrics for Carbon Water, Web 21 May 2019, https://www.datacenterknowledge.com/archives/2010/12/02/green-grid-creates-metrics-for-carbon-water

Attachment

APT Members' Responses to Questionnaire on green data center practices and climate resilience in the Asia-Pacific regions.